## Check-list
QuantaStor 5 Pre-Go-Live & Deployment Check-list
When preparing QuantaStor systems for customers please use the following checklist to ensure consistent and smooth deployments. Please notify OSNEXUS support if you find any missing steps or other considerations which should be added.
Verification Check Step | Description | Quick Config Steps | Check Status | Notes
Review all items, description, and update Check Status |  |  | Verified / Problem
Firmware Verification
Check and upgrade disk firmware to latest version as needed | Disk firmware should be updated to ensure proper functioning with latest generation of HBAs. Especially important for latest generation of high-capacity drives. | N/A
Check and upgrade HBA firmware to latest version as needed | HBA firmware should be updated to ensure proper functioning with latest generation of hardware. Especially important for latest generation of HBA's. | N/A
Check and upgrade RAID controller firmware for boot devices to latest version as needed | Ensures compatilibity with latest disks and SSD devices. | N/A
Check and upgrade motherboard/BIOS firmware to latest version | Ensures compatibility with latest adapters and IPMI support. | N/A
Check and upgrade firmware for disk enclosures / JBOD | Ensures compatability with latest disks, adapters | N/A
Check master list of firmware for components with known issues | https://support.osnexus.com/hc/en-us/articles/360000909843 | N/A
JBOD Cabling
Verify each server SAS HBA is only connected to a given SAS JBOD once per HBA. | See cabling diagram for detailed instructuions. QuantaStor enclosure view will present a [CBLERR] status if improper cabling is detected. (Ceph based configurations) For Ceph configurations with a JBOD per server only a single cable should be used to connect the server HBA to the JBOD as Ceph deployments often use enterprise SATA media. Additionally, multipathing is not supported in Ceph so SAS HDD/SSD media must only be connected via a single cable connection else OSD and Journal device provisioning will fail. In Ceph configurations use a shared-nothing model so JBODs should not be shared between servers as would be done in a ZFS configuration. | N/A
Verify labeling to reflect the above | All cables must be labeled so that customer can re-cable the system after shipping with ease. | N/A
Disk Placement
(ZFS based configurations) Disks should be placed evenly across JBODs so that Storage Pools can be provisioned in an Enclosure-Redundant fashion. | If in a RAID60 setup with 3 enclosures, two disks in each VDEV should be in each enclosure. In a mirror setup with 2 enclosures, one disk in each VDEV should be in each enclosure. For ZIL devices, make sure each VDEV is spread across enclosures. For spares, ensure they are evenly spread across enclosures to provide the possibility of redundancy. In all cases, the goal is to allow for an enclosure-level failure with continued service. After provisioning Storage Pools verify that they are marked as Enclosure Redundant. ZIL or other disks or SSDs that will be used in Storage Pool(s) that are in the server/head unit must be moved to the JBOD(s). | Controllers & Enclosures -> Enclosure View -> verify no enclosures are marked with CBLERR
(Ceph based configurations) Disks should be placed evenly across servers so that Storage Pools can be provisioned with a balanced weighting per server using erasure-coding or replicas. | Ensure that each server has SSDs added in pairs so that the journal (WAL) and metadata offload volumes can be setup in a RAID1 mirror. For SAS/SATA SSD hardware RAID1 is an option for journal mirroring. With NVMe only software RAID1 is an option and the customer must deploy with QuantaStor 5.6 or newer. | Controllers & Enclosures -> Enclosure View -> verify no enclosures are marked with CBLERR
Boot/RAID1 Setup
Create a mirrored/RAID1 boot device using 2x SSDs | Many servers have 2x SFF disk slots which are ideal for the boot drives, these should be used when available. Initial setup of the RAID1 mirror is done via the RAID controller boot time BIOS. This can be configured remotely via IPMI. If the boot disks are in a JBOD, move them into the head unit(s). LSI RAID or OEM equivalent card should be used, not software RAID. SATADOMs should be avoided but there is a software RAID1 option for booting QuantaStor but requires special approval from OSNEXUS Support Engineering. | N/A
Network Setup
Ensure proper SFPs/Cables are used | In some cases, NICs/ports are disabled if the proper (branded) SFPs are not used even if the physical port is the same | Review switch, kernel and syslog for any cable SFP+ / connector errors
Verify that connectivity is available on all types of network interfaces to be used | All NICs should be set up and pinged to ensure they are working properly. This is to ensure that the right cables are used and drivers are properly loaded. | Storage System->Network Ports
Gather network IPs from customer to be setup on the box (IPMI, heartbeat ports / a pair ideally not in the same subnet, data ports) | If the customer cannot provide network IP information use 10.0.x.x or 192.168.x.x networks and provide customer with information on which IPs were selected for the default configuration. | N/A
Setup IPMI port with IPs provided from customer | If the customer cannot provide network IP information use 10.0.x.x or 192.168.x.x networks and provide customer with information on which IPs were selected for the default configuration. | Motherboard BIOS
Connect 1GbE ports to network with DHCP server | If the customer cannot provide network IP information use 10.0.x.x or 192.168.x.x networks and provide customer with information on which IPs were selected for the default configuration. | N/A
Install QuantaStor OS
Install latest version of QuantaStor OS on mirrored boot device | Always install the latest version of QuantaStor available from www.osnexus.com/downloads. Do not use IPMI redirect to install; always use physical media to avoid issues. | N/A
QuantaStor Storage Grid setup
Login via QuantaStor web interface to the IP presented after the appliance reboots post-install | Verify Web UI access and proper installation. The IP address for the appliance will appear at the console screen and is set via DHCP. If there is no DHCP server available to issue the initial IP address from then one must login and set the IPs using the qs CLI or via editing the /etc/network/interfaces file. We recommend using the 'qs np-*' commands. Use qs help=np to see a list of network port configuration commands including qs np-modify. | https://ip-address-of-quantastor-server
Add license key (each box needs a unique key) | Contact OSNEXUS sales for license keys if you do not already have them. If the systems are in the PoC stage full-function but time limited Trial license keys will be issued. | Storage Management -> Storage System -> Licensing -> Add License
Setup network ports per customers specifications (IP address, subnet, jumbo frames, etc) | 10GbE and faster network ports should be configured with jumbo frames enabled | Storage Management -> Storage System -> right-click on network port -> Modify Network Port...
Adjust firewall settings and disable iSCSI on 1GbE management ports | Ensures higher security and that iSCSI traffic is routed over the 10GbE or faster ports | same
Create Storage Grid | QuantaStor combines appliances together to form a Storage Grid. This is done by logging into the first QuantaStor system via the WUI and then subsequently adding the other nodes/systems to the grid. Once the grid is setup it is easy to then setup remote replication and storage clusters within the grid. | Storage Management -> Grid Management -> Create Grid
Add second appliance to grid (repeat for each additional node) | Add systems/appliances to the grid one by one until all of them appear in the Storage Systems section. | Storage Management -> Grid Management -> Add Appliance
Cluster Resource Setup | Required for IP addresses that can move between systems to ensure continuous availability to client connections.
Create Site Cluster (HA Cluster) | Typically eth0 and eth1 are used as management and heartbeat ports. The same ports must be used on each appliance. If the customer doesn't have 1GbE switch ports then the 1GbE ports can be direct connected from server to server. Once the grid is formed cluster(s) can be setup so that pools can be made highly-available. | Cluster Resource Management -> Create Site Cluster
add a cluster ring to the site cluster so that there is a redundant heartbeat in place | All cluster pairs must have dual redundant heart-beat rings | Cluster Resource Management -> Add Cluster Ring
Ceph Cluster Setup (Ceph configurations only)
Create a new Ceph Cluster or add systems to an existing cluster. | Verify that all the systems are in the QuantaStor Storage Grid and then create the Ceph Cluster via the Scale-out Cluster Management tab - > Create Cluster dialog. For clusters with separate front-end and back-end networks be sure to choose the appropriate IPs for these nextworks from the drop-down selection list. | Scale-out Storage Configuration --> Create Cluster
Add OSDs and Journal devices to the cluster | Select OSD creation dialog then select the data devices to be used as OSDs and the SSD devices to be used as journals. Default settings will allocate a 3GB mirrored WAL and 30GB metadata offload volume per OSD. Journal devices must be specified in pairs as they'll be automatically RAID1 mirrored. | Scale-out Storage Configuration --> Create OSDs
Storage Pool Configuration Steps (CephFS based configurations only)
Add MDS server to first server & second servers. | Select "Add MDS Service" to add the file storage metadata service to the first system. Then repeat this stop to add a second MDS service to the second system in the cluster. | Scale-out Storage Configuration --> Add MDS
Create the scale-out Storage Pool (CephFS based) | Navigate to the Scale-out Storage Pools section and create a file Storage Pool (CephFS based). | Scale-out Storage Configuration --> Scale-out Storage Pools -> Create File System
Create a Network Share | Create a Network Share in the newly created Storage Pool and then verify access to it via SMB from a Windows or Linux system. | Storage Management -> Network Shares -> Create Share
Storage Pool Configuration Steps (ZFS based configurations only)
Create a Storage Pool using the devices from the JBOD | Create pool with redundancy in mind; status can be seen after creation "Enclosure Redundancy" for each created pool | Storage Pools -> Create
Add cache and log/ZIL SSD devices to the pool | Boost performance for small-block IO, databases, and VMs using ZIL devices. In general the L2ARC has lower utility and additional ZIL devices should be added where they can offer greater advantage. | Storage Pools -> select pool -> Add Cache Devices
Create HA Pool Group | Once a pool is created, an HA group must be added to it in order to associate VIFs with the pool and to make it highly-available. | Storage Pools -> select pool -> Add HA Group
Add virtual IP for the pool to the HA pool group | All client traffic for SMB, NFS, and iSCSI protocol access to file and block storage must be through the VIFs associated with a given storage pool. VIFs should be on separate networks from the management port network. | Storage Pools -> select pool -> Add HA VIF
Test HA failover | Test client connectivity during failover events to be sure all works well | Storage Pools->Right-click pool->Execute Failover
reboot boxes to ensure automatic pool startup | Verify proper server startup, check logs and IPMI information to verify hardware health including fans and power supplies | Storage System -> select system -> review properties
whitelist new disks for multipathing | By default, only a few models are automatically seen as multipathing devies. Add each model of disk that supports multipathing and re-scan. This must be done for every storage system in the grid | Physical Disks->Multipath Config; Scan
Security Checks
Set default security policy in Security Manager | Via the web interface open the Security Manager and select Suggested Defaults to configure the systems with NIST 800-53 defaults. | Users & Groups -> Security Manager -> Suggested Defaults
Change the Linux console qadmin password | Main qadmin password should be changed from qadmin to something else on each appliance | Console / SSH on each appliance
Change the QuantaStor admin password | Main admin password should be changed from 'password' to something else then re-login | Users & Groups -> select 'admin' -> Change Password
Change the storage grid keys and default CA cert (high-security) | For high-security environments we recommend following the steps on the wiki to change out the CA cert | https://wiki.osnexus.com/index.php?title=Custom_SSL_TLS_Security
Update firewall rules (high-security) | Turn off ports for protocols and services that are not going to be used. | https://wiki.osnexus.com/index.php?title=Firewall_Configuration
Add custom Roles and Users | Add custom roles for additional admins which limit there authorized operation list following the rule of least privledge | Users & Groups -> Add Role / Users & Groups -> Add User
Alert Manager Configuration
Setup one or more call-home mechanisms | Configure one or more of Email, Slack, Pagerduty or other call-home mechanism via the "Alert Manager" dialog. This is accessiable in the main Storage Management tab in the toolbar. Alerts are generated when the systems require maintenance. | Storage Management --> Alert Manager
Final Configuration and Burn-in
Send log report via web interface for each appliance | Verify full logs were recorded and review logs looking for any issues/errors reported. | Storage Management -> right-click appliance -> Send Log Report..
Run load test on appliance for 4+ hours | Login via SSH and use iozone3 or fio to generate load. Contact support@osnexus.com for specific guidance.

## Work-In-Process (hidden)
QuantaStor Pre-Deployment Checklist
The objective of the PreGoLive process is to prepare a turnkey QuantaStor storage appliance prior to delivery to the end-user. Please follow the set-up and initial configuration checklist below and confirm completion of with each verification step.
Distributor/Reseller Partner: |  | End User Name: | End User Storage Workload: |  | Date:
Verification Step |  | Description | Quick Config Steps | Check Status | Notes
Review all items, description, and update Check Status |  |  |  | Verified / Problem
Firmware Verification
1 | Check and upgrade disk firmware to latest version as needed | Disk firmware should be updated to ensure proper functioning with latest generation of HBAs. Especially important for latest generation of high-capacity drives. | N/A | -
2 | Check and upgrade HBA firmware to latest version as needed | HBA firmware should be updated to ensure proper functioning with latest generation of hardware. Especially important for latest generation of HBA's. | N/A | -
3 | Check and upgrade RAID controller firmware for boot devices to latest version as needed | Ensures compatilibity with latest disks and SSD devices. | N/A | -
4 | Check and upgrade motherboard/BIOS firmware to latest version | Ensures compatibility with latest adapters and IPMI support. | N/A | -
5 | Check and upgrade firmware for disk enclosures / JBOD | Ensures compatability with latest disks, adapters | N/A | -
6 | Check master list of firmware for components with known issues | https://support.osnexus.com/hc/en-us/articles/360000909843 | N/A | -
JBOD Cabling
7 | Verify each HBA is only connected to a given JBOD once | See cabling diagram for detailed instructuions. QuantaStor enclosure view will present a [CBLERR] status if improper cabling is detected. | N/A | -
8 | Verify labeling to reflect the above | All cables must be labeled so that customer can re-cable the system with ease after shipping. | N/A | -
Disk Placement
9 | Disks should be placed evenly across JBODs so that Storage Pools can be provisioned and kept Enclosure Redundant. After provisioning Storage Pools verify that they are marked as Enclosure Redundant. ZIL or other disks or SSDs that will be used in Storage Pool(s) that are in the server/head unit must be moved to the JBOD(s). | If in a RAID60 setup with 3 enclosures, two disks in each VDEV should be in each enclosure. In a mirror setup with 2 enclosures, one disk in each VDEV should be in each enclosure. For ZIL devices, make sure each VDEV is spread across enclosures. For spares, ensure they are evenly spread across enclosures to provide the possibility of redundancy. In all cases, the goal is to allow for an enclosure-level failure with continued service. | Controllers & Enclosures -> Enclosure View -> verify no enclosures are marked with CBLERR | -
Boot/RAID1 Setup
10 | Create a mirrored/RAID1 boot device using 2x SSDs | Many servers have 2x SFF disk slots which are ideal for the boot drives, these should be used when available. Initial setup of the RAID1 mirror is done via the RAID controller boot time BIOS. This can be configured remotely via IPMI. If the boot disks are in a JBOD, move them into the head unit(s). LSI RAID or OEM equivalent card should be used, not software RAID. Exception is made for systems with SATADOMs. These are detected and managed and monitored by QuantaStor. | N/A | -
Network Setup
11 | Ensure proper SFPs/Cables are used | In some cases, NICs/ports are disabled if the proper (branded) SFPs are not used even if the physical port is the same | Review switch, kernel and syslog for any cable SFP+ / connector errors | -
12 | Verify that connectivity is available on all types of network interfaces to be used | All NICs should be set up and pinged to ensure they are working properly. This is to ensure that the right cables are used and drivers are properly loaded. | Storage System->Network Ports | -
13 | Gather network IPs from customer to be setup on the box (IPMI, heartbeat ports / a pair ideally not in the same subnet, data ports) | If the customer cannot provide network IP information use 10.0.x.x or 192.168.x.x networks and provide customer with information on which IPs were selected for the default configuration. | N/A | -
14 | setup IPMI port with IP from customer | If the customer cannot provide network IP information use 10.0.x.x or 192.168.x.x networks and provide customer with information on which IPs were selected for the default configuration. | Motherboard BIOS | -
15 | connect 1GbE ports to network with DHCP server | If the customer cannot provide network IP information use 10.0.x.x or 192.168.x.x networks and provide customer with information on which IPs were selected for the default configuration. | N/A | -
Install QuantaStor OS
16 | Install latest version of QuantaStor OS on mirrored boot device | Always install the latest version of QuantaStor available from www.osnexus.com/downloads. Do not use IPMI redirect to install; always use physical media to avoid issues. | N/A | -
QuantaStor Storage Grid setup
17 | Login via QuantaStor web interface to the IP presented after the appliance reboots post-install | Verify Web UI access and proper installation. The IP address for the appliance will appear at the console screen and is set via DHCP. If there is no DHCP server available to issue the initial IP address from then one must login and set the IPs using the qs CLI or via editing the /etc/network/interfaces file. We recommend using the 'qs np-*' commands. Use qs help=np to see a list of network port configuration commands including qs np-modify. | N/A | -
18 | Add license key (each box needs a unique key) | Contact OSNEXUS sales for license keys if you do not already have them. If the systems are in the PoC stage full-function but time limited Trial license keys will be issued. | Storage Management -> Storage System -> Licensing -> Add License | -
19 | Setup network ports per customers specifications (IP address, subnet, jumbo frames, etc) | 10GbE and faster network ports should be configured with jumbo frames enabled | Storage Management -> Storage System -> right-click on network port -> Modify Network Port... | -
20 | disable iSCSI on 1GbE management ports | Ensures iSCSI traffic is routed over the 10GbE or faster ports | same | -
21 | Create storage grid | QuantaStor combines appliances together to form a storage grid. In order to setup a HA pool, remote replication, or scale-out clusters one must first create a grid and add all appliance to it. | Storage Management -> Grid Management -> Create Grid | -
22 | Add second appliance to grid (repeat for each additional node) | Add appliances to the grid one by one until all of them appear in the Storage Systems section. | Storage Management -> Grid Management -> Add Appliance | -
HA Cluster setup
23 | Create Site Cluster (HA Cluster) | Typically using eth0 and eth1 as heartbeat ports. The same ports must be used on each appliance. If the customer doesn't have 1GbE switch ports then the 1GbE ports can be direct connected from server to server. Once the grid is formed cluster(s) can be setup so that pools can be made highly-available. | Cluster Resource Management -> Create Site Cluster | -
24 | add a cluster ring to the site cluster so that there is a redundant heartbeat in place | All cluster pairs must have dual redundant heart-beat rings | Cluster Resource Management -> Add Cluster Ring | -
SAN/NAS Configuration Steps |  | Specific configuration steps for setting up highly-available SAN/NAS configurations (most common)
25 | Create a storage pool using the devices from the JBOD | Create pool with proper RAID layout; status can be seen after creation "Enclosure Redundancy" for each created pool | Storage Pools -> Create | -
26 | Add cache and log/ZIL SSD devices to the pool | Boost performance for small-block IO, databases, and VMs using ZIL devices. In general the L2ARC has lower utility and additional ZIL devices should be added where they can offer greater advantage. | Storage Pools -> select pool -> Add Cache Devices | -
27 | Create HA Pool Group | Once a pool is created, an HA group must be added to it in order to associate VIFs with the pool and to make it highly-available. | Storage Pools -> select pool -> Add HA Group | -
28 | Add virtual IP for the pool to the HA pool group | All client traffic for SMB, NFS, and iSCSI protocol access to file and block storage must be through the VIFs associated with a given storage pool. VIFs should be on separate networks from the management port network. | Storage Pools -> select pool -> Add HA VIF | -
29 | test HA failover | Test client connectivity during failover events to be sure all works well | Storage Pools->Right-click pool->Execute Failover | -
30 | reboot boxes to ensure automatic pool startup | Verify proper server startup, check logs and IPMI information to verify hardware health including fans and power supplies | Storage System -> select system -> review properties | -
31 | whitelist new disks for multipathing | By default, only a few models are automatically seen as multipathing devies. Add each model of disk that supports multipathing and re-scan. This must be done for every storage system in the grid | Physical Disks->Multipath Config; Scan | -
Security Checks
32 | Set default security policy in Security Manager | Via the web interface open the Security Manager and select Suggested Defaults to configure the systems with NIST 800-53 defaults. | Users & Groups -> Security Manager -> Suggested Defaults | -
33 | Change the Linux console qadmin password | Main qadmin password should be changed from qadmin to something else on each appliance | Console / SSH on each appliance | -
34 | Change the QuantaStor admin password | Main admin password should be changed from 'password' to something else then re-login | Users & Groups -> select 'admin' -> Change Password | -
35 | Change the storage grid keys and default CA cert (high-security) | For high-security environments we recommend following the steps on the wiki to change out the CA cert | https://wiki.osnexus.com/index.php?title=Custom_SSL_TLS_Security | -
36 | Update firewall rules (high-security) | Turn off ports for protocols and services that are not going to be used. | https://wiki.osnexus.com/index.php?title=Firewall_Configuration | -
37 | Add custom Roles and Users | Add custom roles for additional admins which limit there authorized operation list following the rule of least privledge | Users & Groups -> Add Role / Users & Groups -> Add User | -
Final Configuration and Burn-in
38 | Send log report via web interface for each appliance |  | Storage Management -> right-click appliance -> Send Log Report.. | -
39 | Run load test on appliance for 4+ hours | Login via SSH and use iozone3 or fio to generate load. Contact support@osnexus.com for specific guidance. |  | -
OSNEXUS Certification: |  | Reviewed By: | Date: |  | Signature:
For OSNEXUS assistance, contact sdr@osnexus.com Please notify OSNEXUS if you find any missing verification steps or other information that should be added.

## validation data (hidden)
Column E
Check Status
-
Verified
Problem